## HV Equipment
Student Name: Zahra Iranpour |  |  |  | 1402/04/11
Project Name: 132kv swithcing- 2in/3out- each line 150MVA- double busbar
Item | Description | QUANTITY
|  | MAIN | SPARE (10% Main) | TOTAL
1 | kV CB Circuit Breaker | 6 | 1 | 7
2 | kV DS Disconnect Switch | 17 | 2 | 19
3 | kV CT Current Transformer | 6 | 1 | 7
4 | kV CVT Capacitive Voltage Transformer | 7 | 1 | 8
5 | kV SA Surge Arrester | 5 | 1 | 6
6 | kV LT Line Trap | 5 | 1 | 6
%70-%110
%85-%110

## 132kV CB
Manufacturer:
Item | Description | Unit | Guaranteed Characteristic | Qty.
I | 132kV CIRCUIT BREAKERS |  |  | 7 SET
1 | DESIGNATION
1.1 | -Type |  | SF6
1.2 | -Electrical reference standard |  | IEC 62271-100
1.3 | -Number of poles per ciruit breaker |  | 2
1.4 | -Number of intrupting unit per pole |  | 1
1.5 | -Type of control mechanism
1.6 | -Height above sea level | m | 1000
1.7 | -Circuit breaker class
1.8 | -Minimum and maximum ambient temperature | ºC | -10 / 50
1.9 | -Max siesmic factor | g | 0,4
1.1 | -Pollution level |  | very heavy
1.11 | -Ice thickness | mm | 10
1.12 | -Max wind velocity (normal/gust) | m/s | 30 / 40
1.13 | -Max related humidity | % | 80
1.14 | -System neutral earthing
2 | Main characteristics
2.1 | -Rated voltage : | KV | 132
2.2 | -Max. rated voltage : | KV | 145
2.3 | -Rated normal current( at site condition) : | A | 796
2.4 | -Rated short time withstand current | KA/s | 40,
3 | Rated insulation level (At sea level, IEC conditions)
3.1 | -Rated one minute power frequency withstand voltage
3.1.1 | common value | KV(rms)
3.1.2 | across open breaker | KV(rms)
3.2 | -Rated lightning impulse withstand voltage
3.2.1 | common value | KV(peak)
3.2.2 | across open breaker | KV(peak) | 650
3.3 | -Rated switching impulse withstand voltage
3.3.1 | phase /earth , phase / phase | KV(peak) | 0
3.3.2 | across open breaker | KV(peak)
4 | Insulators
4.1 | - Type
4.2 | -Min. creepage distance across terminals | mm | 4495

## 132kV DS & DSE
Manufacturer:
Item | Description | Unit | Guaranteed Characteristic | QTY
A | 132 KV DISCONNECTORS WITH EARTHING SWITCH |  |  | 19 SET
1 | Designation
1.1 | Standard : |  | IEC 62271/102
1.2 | Type of mechanism: DS/ES
1.3 | Frequency | Hz | 50
1.4 | Max. sys. voltage | kV | 132
1.5 | Nominal voltage | kV | 145
1.6 | Number of poles
1.7 | Class
1.8 | Height above sea level | m | 1000
1.9 | Max. Related humidity | % | 80
1.1 | Siesmic factor | g | 0.4
1.11 | Pollution level |  | very heavy
1.12 | Ice thickness | mm | 10
1.13 | Wind velocity (normal/gust) | m/s | 30 / 40
1.14 | System neutral earthing
2 | Rated insulation level (At sea level, IEC conditions)
2.1 | Rated lightning impulse withstand voltage:
2.1.1 | -Common Value | kV peak
2.1.2 | -Across the isolating distance | kV peak | 345
2.2 | Rated 1 min. Power frequency withstand voltage:
2.2.1 | -Common Value | kV rms
2.2.2 | -Across the isolating distance | kV rms
2.3 | Rated switching impulse withstand voltage:
2.3.1 | -Phase to earth | kV peak
2.3.2 | -Between poles | kV peak
2.3.3 | -Across isolating distance | kV peak
3 | Rated Charactristics
3.1 | Phase spacing of poles | m | 2
3.2 | Rated normal current (At site service condition, only for DS) | A rms | 917
3.3 | -Rated short time withstand current(for disconnector) | KA(rms)/s
4 | Insulator
4.1 | type
4.2 | Min . creepage distance | mm | 4495

## 132KV - CT
Manufacturer:
Item | Description | UNIT | Guaranteed Characteristic | Qty.
(Including technical specification detail)
| 132KV, SINGLE PHASE CURRENT TRANSFORMER |  |  | 7
1 | DESIGNATION
1.1 | Applicable standard |  | IEC 60044-1&6
1.2 | Type
1.3 | Class
1.4 | Nominal voltage | KV | 132
1.5 | Max. system voltage | KV | 145
1.6 | Rated frequency | Hz | 50
1.7 | Height above sea level | m | 1000
1.8 | Max./Min air temprature | ºC | 50 / -10
1.9 | Max Related humidity | % | 80
1.1 | Max. Siesmic factor | g | 0,4
1.11 | Pollution level |  | very heavy
1.13 | Wind velocity (normal./gust.) | m/s | 30 / 40
1.14 | Ice thickness | mm | 10
1.16 | System neutral earthing
2 | RATED INSULATION LEVEL (AT Sea level & IEC Service Conditions )
2.1 | Rated lightning impulse withstand voltage | KV(peak) | 520
2.2 | Rated switching impulse withstand voltage | KV(peak)
2.3 | One minute power frequency withstand voltage | KV(rms)
3 | RATED CHARACTRISTICS
3.1 | Short time thermal current on all ratios | KA / Sec | 40,
3.5 | Ratio
Core 1 :
Core 2 :
Core 3 :
Core 4 :
9 | Type of insulator
9.2 | Min. creepage distance | mm | 4495
9.4 | Washable in service |  | Yes

## 132KV CVT
Manufacturer:
Item | Description | UNIT | Guaranteed Characteristic | QTY
1 | 132 kV C.V.T. |  |  | 8
1 | Designation
1.1 | Standard |  | IEC 60044-2
1.2 | Type
1.3 | Class
1.4 | Connection in system
1.5 | Nominal voltage | KV | 132
1.6 | Rated frequency | HZ | 50
1.7 | Max. sys. voltage | KV | 145
1.8 | System short circuit level | KA/sec
1.9 | Height above sea level | m | 1000
1.1 | Max./Min air temperature | ºC | 50 / -10
1.11 | Max. Related humidity | % | 80
1.12 | Max. Seismic factor | g | 0,4
1.13 | Pollution level
1.15 | Max.wind velocity (normal./ gust.) | m/s | 30 / 40
1.16 | Ice thickness | mm | 10
2 | Insulation Level (At sea level,IEC service condition)
2.1 | Rated lightning impulse withstand voltage | KV(peak) | 520
2.2 | Rated switching impulse withstand voltage | KV(peak)
2.3 | One minute power frequency withstand voltage | KV(rms)
3 | Rated Characteristics
3.1 | System neutral earthing
3.2 | Voltage Ratio and accuracy class:
winding 1
winding 2
3.4 | Capacitor units
3.4.1 | Min. coupling capacitance | PF | *
3.4.2 | Neutral frequency greater than | MHZ | *
3.4.3 | Equivalent series resistance | Ω | *
3.8 | partial discharge level at Um and 1.2Um/√3 | pC | 10
3.9 | frequency range for PLC usage | KHz | *
3.10 | attenuation of PLC frequencies by intermediate transformer | dB | *
7 | Type of insulator
7.3 | Min. creepage distance | mm | 4495
Note: " * " Should be completed by Manufacturer

## 132kV SA
Manufacturer:
Item | Description | Unit | Type | QTY
(Including technical specification detail)
| 132kV Lightning Arrester |  |  | 6
1 | Designation
1.1 | Standard |  | IEC 60099-4,5
1.2 | Type
1.3 | Class
1.4 | System Nominal voltage | KV | 132
1.5 | Rated frequency | HZ | 50
1.6 | Max. sys. voltage | KV | 145
1.7 | Height above sea level | m | 1000
1.8 | Max./Min air temprature | °C | 50 / -10
1.9 | Max. Related humidity | % | 80
1.1 | Siesmic factor Max. | m/s2 | 0,4
1.11 | Pollution level |  | very heavy
1.13 | Wind velocity (normal/gust) | m/s | 30 / 40
1.14 | Ice Loading | mm | 10
1.16 | System neutral earthing
1.17 | Rated voltage (Ur) | KV (rms)
1.18 | Continuous operating voltage (Uc) | KV (rms)
1.19 | Nominal discharge current (wave 8/20 µs ) | KA(peak)
2 | Residual Voltage
2.1 | Steep current impulse residual voltage at 20 KA(wave 1/20 µs) | KV(peak)
2.1.1 | Lightning impulse residual voltage (wave 8/20 µs ) :
2.1.2 | 5kA | KV(peak) | *
2.1.3 | 10kA | KV(peak) | *
2.1.4 | 20kA | KV(peak) | *
2.2 | Switching impulse residual voltage (wave 30/60 µs ) :
2.2.1 | 500A | KV(peak) | *
2.2.2 | 1000A | KV(peak) | *
2.2.3 | 2000A | KV(peak) | *
3 | EXTERNAL INSULATION LEVEL OF PROTECTION:
3.4 | Min. Creepage distance (ph to ground) | mm | 4495
3.5 | Type of insulator
3.6 | Grading ring provided at live side
3.12 | Type of Surge Counter |  | *
3.13 | Leakage current metering device |  | yes
* | Shall be Completed by Manufacturer.

## LT
Manufacturer: |  |  |  | 0
0
Item | Description | UNIT | Guaranteed Characteristic | Qty.
| LINE TRAP |  |  | 6
1 | Designation
1.1 | Type & Class
1.2 | standard |  | IEC353
1.3 | Method of mounting |  | PI
1.4 | Frequency | Hz | 50
1.5 | Max. sys. voltage | kV | 132
1.6 | Nominal voltage | kV | 145
1.7 | Class |  | 0
1.8 | Height above sea level | m | 1000
1.9 | Max./Min air temprature | OC | -10 ,50
1.11 | Max. Related humidity | % | 80
1.12 | Max. seismic factor | g | 0.4
1.13 | Pollution level |  | very high
1.14 | Ice thickness | mm | 10
1.16 | -Max wind velocity (normal/gust) | m/s | 30/40
3 | Rated Characteristics
3.1 | Rated continuous current (at site service conditions ) | A rms | 245
3.2 | Rated short-time thermal current | kA rms | 40
3.3 | Duration of short-time thermal current | Sec. | 1-3
14 | type of mounting |  | generic electric
8 | Inductance | mH | 1